## 2024_Town_Dam_Month-to-Date_Wat
Form Completed By: | Date and Time of Check-In | Type of Check-In | Hwy 557 Ruler | Dam Ruler (N/A when Logs Out) | Is Water Level In Compliance | Which Ruler is in Compliance? | Weather (temperature in celsius) | WATER TEMPERATURE if required | Water Management Plan Period | Bay 1: TURBINES | Bay 2: 6 Logs Maximum | Bay 3: 8 Logs Maximum | Bay 4: 10 Logs Maximum | Bay 5: MECH GATE MAX 9 Logs | Bay 1 After change: TURBINES | Bay 2 After change: 6 Logs Maximum | Bay 3 after change: 8 Logs Maximum | Bay 4 after change: 10 Logs Maximum | Bay 5 after change: MECH GATE MAX 9 Logs | OOC Comment | Dam Ruler After Log Changes
Colin | 2024-10-31 13:22 | ONSITE both Headpond & Powerhouse |  | 58 | NO |  | 10 |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to mechanical gate leakage and lack of rain,we are expecting a bunch of rain this week hoping level will come up to compliance
Colin | 2024-10-31 11:59 | RULER only 557 bridge | 57 |  | NO |  | 9 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to mechanical gate leakage and lack of rain.we are getting a bunch of rain this week hoping to bring level up
Dana | 2024-10-31 10:18 | RULER only 557 bridge | .56 (.55 to .58 with wind but settles at .56) |  |  |  | 7C rain warning continues |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED
Dana | 2024-10-31 06:32 | RULER only 557 bridge | 0.565 |  | NO |  | 9C, heavy rain (warning up to 60mm over 24 hrs ending Fri) |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Level coming up and should be in compliance today if rain continues as Scarfe is also sending extra water.
Dana | 2024-10-30 22:06 | RULER only 557 bridge | 0.53 |  | NO |  | 15C |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Rain expected to improve and scarfe sending water also
Colin | 2024-10-30 12:08 | ONSITE both Headpond & Powerhouse |  | 52 | NO |  | 18 |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to mechanical gate leakage and lack of rain
Colin | 2024-10-30 09:22 | RULER only 557 bridge | 53 |  | NO |  | 18 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can due to mechanical gate leakage and lack of rain
Colin | 2024-10-29 15:14 | ONSITE both Headpond & Powerhouse |  | 52 | NO |  | 11 |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to mechanical gate leakage and lack of rain
Colin | 2024-10-29 09:33 | RULER only 557 bridge | 53 |  | NO |  | 11 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to mechanical gate leakage and lack of rain we are expecting a bunch of rain this week hoping to bring level up a bit
Matt | 2024-10-28 13:30 | ONSITE both Headpond & Powerhouse |  | 51 | NO |  | 6c |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Leakage,lack of rain.
Matt | 2024-10-28 09:28 | RULER only 557 bridge | 53 |  | NO |  | 4c |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Lack of rain.
Zoran | 2024-10-27 14:42 | RULER only 557 bridge | 0.53 |  | NO |  | 8 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. No water coming from upstream and lack of rain cause levels to be under compliance.
Zoran | 2024-10-26 14:07 | RULER only 557 bridge | 53 |  | NO |  | 10 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. Lack of water upstream and no rain.
Greg | 2024-10-25 12:31 | ONSITE both Headpond & Powerhouse |  |  | NO |  | 11 light rain |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Low water level upstream ( matinenda), working with MNR on leakage to hold water levels, rain forecasted should help water levels
Greg | 2024-10-25 09:20 | RULER only 557 bridge | 53 wavy |  | NO |  | 8 overcast |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Low water levels upstream ( matinenda) working with MNR to control leakage at town dam to hold water levels, rain in forecast should help level
Greg | 2024-10-24 14:48 | RULER only 557 bridge | 53 |  | NO |  | 15 sunny |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Low water upstream ( matinenda) working wit MNR to control leakage at blind river dam to hold levels
Greg | 2024-10-24 11:11 | ONSITE both Headpond & Powerhouse |  | 53 | NO |  | 11 overcast |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Low water levels upstream ( matinenda), working with MNR on leakage at town dam to hold water levels.
Greg | 2024-10-23 14:21 | ONSITE both Headpond & Powerhouse |  | 55 | NO |  | 10 overcast breezy |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Low level upstream ( Matinenda) working with MNR on leakage to help hold levels.
Greg | 2024-10-23 09:58 | RULER only 557 bridge | 53 |  | NO |  | 10 overcast |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Low water level upstream ( Matinenda), and working with MNR to control leakage at town dam to hold levels.
Zoran | 2024-10-22 15:01 | ONSITE both Headpond & Powerhouse |  | 0.53 | NO |  | 20 |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance due to lack of water upstream and a lack of rain.
Colin | 2024-10-22 13:07 | RULER only 557 bridge | 53.5 |  | NO |  | 20 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to mechanical gate leakage and lack of rain hoping to come up a bit with rain expected this week
Greg | 2024-10-21 13:42 | ONSITE both Headpond & Powerhouse |  | 53 | NO |  | 20 sunny |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Working with MNR to slow leakage at town dam to hold water and likely rain to help this week with water levels.
Colin | 2024-10-21 09:33 | RULER only 557 bridge | 53 |  | NO |  | 10 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can with mechanical gate leakage and lack of rain
Dana | 2024-10-20 09:15 | RULER only 557 bridge | 0.54 |  | NO |  | 10c |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | No rain. Matinenda under compliance and not spilling, focusing on sealing town dam (mech gate and under bay 4) better to help hold
Dana | 2024-10-19 09:27 | RULER only 557 bridge | 0.54 |  | NO |  | 5 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | No rain. Matinenda low so unable to release more water from above 557 and working with MNR to correct town dam leakage
Matt | 2024-10-18 14:04 | ONSITE both Headpond & Powerhouse |  | 53 | NO |  | 13c |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Lack of rainfall. Leakage at mech. gate.
Zoran | 2024-10-18 09:41 | RULER only 557 bridge | 0.55 |  | NO |  | 5 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. The lack of water upstream combined with issues with the mechanical gate at the town dam(leakage issue that MNR is aware off) and no significant rain forecast in near future that could change the water level.
Matt | 2024-10-17 13:37 | ONSITE both Headpond & Powerhouse |  | 53 | NO |  | 11c |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Lack of rain. Leakage.
Zoran | 2024-10-17 09:27 | RULER only 557 bridge | 0.55 |  | NO |  | 2 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. No rain, low water upstream (Mat) and leakage at town dam being investigated by MNR to also assist with holding levels.
Greg | 2024-10-16 10:36 | RULER only 557 bridge | 55 |  | NO |  | 8 sunny |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Low water levels upstream ( Matinenda) no rainfall, leakage at town dam being investigated by MNR to help hold water levels.
Greg | 2024-10-16 09:59 | ONSITE both Headpond & Powerhouse |  | 54 | NO |  | 6 sunny |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | No rain,low water level upstream ( Matinenda), MNR is investigating the leakage at town dam to help hold levels.
Matt | 2024-10-15 13:39 | ONSITE both Headpond & Powerhouse |  | 57 | NO |  | 11c |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Lack of rain/Leakage.
Zoran | 2024-10-15 10:09 | RULER only 557 bridge | 0.56 |  | NO |  | 6 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. Holding as much as possible, with mechanical gate leakage and the lack of rain.
Colin | 2024-10-14 08:13 | RULER only 557 bridge | 56 |  | NO |  | 5 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can wth mechanical gate leakage and lack of rain
Colin | 2024-10-13 08:47 | RULER only 557 bridge | 57 |  | NO |  | 6 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to mechanical gate leakage and lack of rain
Colin | 2024-10-12 08:20 | RULER only 557 bridge | 56.5 |  | NO |  | 1 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to mechanical gate leakage and lack of rain
Zoran | 2024-10-11 13:59 | ONSITE both Headpond & Powerhouse |  | 56 | NO |  | 15 |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. Water slow coming from upstream, unusually dry October.
Zoran | 2024-10-11 09:31 | RULER only 557 bridge | 0.57 |  | NO |  | 12 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. Lack of rain, not enough water coming from upstream.
Zoran | 2024-10-10 13:22 | ONSITE both Headpond & Powerhouse |  | 0.56 | NO |  | 15 |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. Small leak under the mechanical gate and no water coming from upstream (lack of rain).
Zoran | 2024-10-10 09:23 | RULER only 557 bridge | 57 |  | NO |  | 3 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. Not enough water coming from upstream due to lack of rain. The leakage under mechanical gate at the town dam is being looked at by MNR.
Zoran | 2024-10-09 13:38 | ONSITE both Headpond & Powerhouse |  | 0.58 | NO |  | 13 |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. Leak at the mechanical gate is being checked by MNR.
Zoran | 2024-10-09 09:29 | RULER only 557 bridge | 0.57 |  | NO |  | 8 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance . The leak at the mechanical gate will be looked at by MNR.
Colin | 2024-10-08 13:10 | ONSITE both Headpond & Powerhouse |  | 58 | NO |  | 16 |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to mechanical gate leakage and lack of rain
Colin | 2024-10-08 09:22 | RULER only 557 bridge | 57 |  | NO |  | 9 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to leak in mechanical gate and lack of rain
Colin | 2024-10-07 14:34 | ONSITE both Headpond & Powerhouse |  | 58 | NO |  | 17 |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding the best we can do to mechanical gate leakage and lack of rain
Colin | 2024-10-07 09:25 | RULER only 557 bridge | 57 |  | NO |  | 10 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Holding best we can do to leak in mechanical gate and lack of rain
Zoran | 2024-10-06 14:09 | RULER only 557 bridge | 0.58 |  | NO |  | 17 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. Water coming down from upstream after this weekend rain.
Zoran | 2024-10-05 10:33 | RULER only 557 bridge | 0.59 |  | NO |  | 14 |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Under compliance. Expecting rain over the weekend to raise the level.
Greg | 2024-10-04 15:22 | ONSITE both Headpond & Powerhouse |  | 50 | NO |  | 18 breezy |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Water is on its way and lots of precipitation in near forecast
Greg | 2024-10-04 12:36 | RULER only 557 bridge | 59 |  | NO |  | 20 sunny |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Low water level upstream ( matinenda) rain in the forecast should help water level
Greg | 2024-10-03 15:04 | ONSITE both Headpond & Powerhouse |  | 59 | NO |  | 22 overcast |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Low water levels upstream ( Matinenda) so will continue to hold, water is on its way.
Greg | 2024-10-03 14:22 | ONSITE both Headpond & Powerhouse |  | 59 | NO |  | 20 sunny and breezy |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Everything is closed up top due to low water levels at ( Matinenda). Rain in the forecast should help levels.
Greg | 2024-10-03 09:15 | RULER only 557 bridge | 59 |  | NO |  | 15 sunny |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED | [5 empty] | Low water level upstream ( Matinenda) hoping rainfall in the forecast will bring level up.
Greg | 2024-10-02 14:10 | ONSITE both Headpond & Powerhouse |  | 59 | YES | 557 ruler | 16 breezy |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED
Greg | 2024-10-02 09:31 | RULER only 557 bridge | 60 |  | YES | 557 ruler | 14 sunny |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED
Greg | 2024-10-01 14:28 | ONSITE both Headpond & Powerhouse |  | 59.5 | YES | 557 ruler | 15 overcast |  | Oct. 1 to Nov. 30 | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED
Greg | 2024-10-01 09:55 | RULER only 557 bridge | 60 |  | YES | 557 ruler | 18 overcast |  | Oct. 1 to Nov. 30 |  | 1 Log Out | 1 Log Out | 1 Log Out | NO LOGS OUT - GATE CLOSED